Valve controller documentation draft 26.12.2014

# Controller board pins assignment
The valve controller is operated by a TI MSP430 LaunchPad development board with msp430g2553 controller.
Controller pins are assigned the following way:
Pin	Function	Direction	States
VCC	3.3 V power	IN	N/A
P1.0	N/C (Integrated red LED)	N/C	N/A
P1.1	N/C (Integrated UART)	N/C	N/A
P1.2	N/C (Integrated UART)	N/C	N/A
P1.3	N/C (Integrated button)	N/C	N/A
P1.4	ADC Vref+	IN	Vref/5 analog signal (around 2V DC)
P1.5	ADC Ch.5	IN	Vtrig/5 analog signal
P1.6	N/C (Integrated green LED)	N/C	N/A
P1.7	ADC Ch.7	IN	Vin/5 analog signal
P2.0	MCU mode out, / activated by internal switch	OUT	High: output enabled, valve open / Low: output disabled, valve closed
P2.1	Mixed mode close	OUT	High: normal operation / Low: short pulse to activate the trigger and disable the output(close the valve)
P2.2	N/C	N/C	N/A
P2.3	Mixed mode open	OUT	High: short pulse to activate the trigger and enable the output (open the valve) / Low: normal operation
P2.4	Valve state indicator	IN	MCU internal pull-up to high, / LOW: valve closed
P2.5	Valve state indicator	IN	MCU internal pull-up to high, / LOW: valve open
GND	Board ground level	IN	N/A

# Serial interface
Valve controller emulates a serial port and is operated using a simple serial-based protocol.
## Serial port settings
9600 bit/s, 8 bytes, 1 stop bit, no parity control.
Setting of any bitrate higher than 9600 is internally overriden to 9600 bit/s by the USB-Serial converter.
## Communication protocol
Valve controller supports a limited set of single-character commands. There is no need to follow the command by CR-LF sequence. Controller immediately responds with a sequence of lines, each terminated by CR-LF sequence.
A summary of commands is provided in the following table:
Command	Symbol	Detailed description
Identify	i	Print the board identification string.
Get Voltages	v	Print threshold voltage, corresponding pressure, actual input voltage and corresponding pressure. / Response format is the following: / Vtrig: 3499mV / Ptrig: 5.4E-8Torr / Vin: 57mV / Pin: 1.4E-11Torr
Get valve position	p	Get the valve position indicator status. Possible answers are: / UNDEF Both position switches read as open or closed. / OPEN Position switch “open” reads as 0, “close” as 1 / CLOSED Position switch “open” reads as 1, “close” as 0
Close the valve	c	Immediately send a trigger pulse to close the valve, / deactivate the digital output. Returns “OK” as a confirmation
Open the valve	o	Check that Vin<Vthresh, send a trigger pulse to open the valve and activate the output if true. / Returns “OK” if the operation succeded. / Returns “PERR” if Vin>=Vthresh.
Unknown command	any	Board responds with a string “Unknown command” to any invalid symbol.